## Slide 1: Leakage Model Development Proposals – Shrinkage Forum Discussion
Wednesday 14 December 2011

## Slide 2: Proposals
Two proposed changes to the National Leakage Model to improve its accuracy
  Update low pressure service population assumptions
  Update AGI Venting calculation

## Slide 3: Why are we proposing these modifications now?
Transporters have to submit final business plans for RIIO-GD1 in April 2012. These will include our leakage projections.
  We believe the proposed modifications provide for a more accurate and robust estimation of leakage and that these should be reflected in the baseline allowances
  The current Transporter Licence requires Transporters to consult on modifications to the leakage model; this process takes two-three months

## Slide 4: Low Pressure Service Modification - Background
Existing Metallic Main
  Mixture of Steel and PE Services
  Steel Service Leakage Rate 10.6m3 p.a. per service
  PE Service Leakage Rate 2.2m3 p.a. per service
Existing PE Main
  Predominantly PE Services (est 98%)
  PE and Steel connections to PE mains found not to leak (2002/03 National Leakage Tests)
Notes: Metallic mains tend to have a mixture of Steel and PE services.
Some steel services may have been ‘replaced’ following gas escapes
PE mains have predominantly PE services. Current policy is to not reconnect steel services; however, historically, a steel service could be reconnected if, after testing, it was found not to be leaking.

## Slide 5: Low Pressure Service Modification - Mains Replacement
Mains Replacement
  Steel service connections ‘re-laid’ in PE and connected to new main
  PE service connections ‘transferred’ to new main

## Slide 6: Low Pressure Service Modification - Current Model
Current Methodology
  No. of Metallic Services determined using the original model applied up to 2006/07 (the year used to establish GDPCR1 baselines)
  No. of replaced services deducted from starting values
Issues
  Original model service population assumptions date back to early 1990s
    Major assumption in original model is that a fixed proportion (one-third) of all services on mixed material networks are metallic
    Condition replacement of services from early 1990s to 2006/07 not reflected in estimate
  National assumption, i.e. same service population assumption for each LDZ

## Slide 7: Low Pressure Service Modification - Proposed Model
New method of estimating the number of PE and Steel Services
  Use the latest service ‘Re-lay’ and ‘Transfer’ data associated with mains replacement to estimate current population of metallic and plastic services, respectively
  Use data from mains replacement work as representative of population as a whole
  Determine No. services per km of metallic main
  Propose to use three years mains replacement data to provide robust sample (6000km in comparison to 43,000km remaining for National Grid)
  Establish a new Network specific baseline service population for 2010/11
Going Forward
  As in the current model, no. of replaced services deducted from ‘Steel Service to Metal Main’ starting values
  In addition, no. of transferred services deducted from ‘PE Service to Metal Main’ starting values
Notes: Connections to PE mains have a zero leakage rate; however, propose to use the proportions identified from the 2002/03 NLT to allocate these in the model.

## Slide 8: Low Pressure Service Modification – Number of Transfers and Re-lays
 |  | 2008/09 | 2009/10 | 2010/11 | Length Weighted Avg
Transfers /km | EoE | 43 | 46 | 43 | 44
 | LN | 45 | 29 | 22 | 31
 | NW | 31 | 32 | 31 | 31
 | WM | 37 | 36 | 30 | 35
Re-lays /km | EoE | 41 | 41 | 44 | 42
 | LN | 31 | 45 | 46 | 39
 | NW | 47 | 44 | 42 | 45
 | WM | 47 | 53 | 53 | 51
Notes: Transfers deemed to be representative of existing plastic service connections to metallic mains
Re-lays deemed to be representative of existing metallic service connections to metallic mains
3 years RRP data reflects the replacement of 6,200km of metallic main, there is currently 43,000km metallic main remaining.

## Slide 9: Low Pressure Service Modification – How will this work?
E.g. for East of England
Connections to Metallic Mains =
  Steel Service connections to metallic mains = Re-lay Rate (42/km) x length of metallic main
  +
  PE Service connections to metallic mains = Transfer Rate (44/km) x length of metallic main
Connections to PE mains = Total Number of Services – Connections to Metallic Mains
  PE Service connections to PE Mains = 98% x Connections to PE Mains
  Steel Service connections to PE Mains = 2% x Connections to PE Mains
Notes: Total number of services is assumed to be the total number of meter points

## Slide 10: Low Pressure Service Modification - Impact on Leakage Assessment
LDZ | 2010/11 Leakage GWh |  |  | 
 | Current Model | Proposed Model | Change | 
EA | 228 | 216 | -12 | -5%
EM | 321 | 297 | -24 | -8%
NT | 346 | 314 | -32 | -9%
NW | 428 | 410 | -17 | -4%
WM | 345 | 341 | -4 | -1%
 | 1,667 | 1,578 | -89 | -5%

## Slide 11: Low Pressure Service Modification – Metallic service proportion (mixed material networks)
 | Metal Service Proportion
EA | 21%
EM | 19%
NT | 18%
NW | 23%
WM | 29%
National Grid | 22%
Notes: Application of the proposed methodology suggests that 22% of services on mixed material networks are metallic, compared with the original one-third assumption. A reduction in this is to be expected as the majority of new services and services connected to replaced mains will be plastic.

## Slide 12: Low Pressure Service Modification - Benefits
Service population assumptions are more up-to-date and Network specific
Better estimate of forward leakage reduction associated with service replacement, as PE transfers taken into account

## Slide 13: AGI Venting - Current Model
Current Methodology
  ‘Fixed’ values based on a 1994 Watt Committee report
    National estimate
    Derivation unknown
  National value apportioned across LDZs at time of Network Sale
  Approximately 5% of over all emissions

## Slide 14: AGI Venting -Background
Two routinely venting components
  Positioners
  Controllers
Venting occurs both in steady state and during control actions
Each AGI usually has a number of Positioners and Controllers
Positoners and Controllers originally designed to work with compressed air but modified to work with gas, as readily available on site.

## Slide 15: AGI Venting - Pneumatic Control Mechanism

## Slide 16: AGI Venting - Proposal
Proposed Methodology
  Use manufacturers published data to estimate steady state venting
  Actual emissions used in operation difficult to estimate, as depends on number of control actions. Propose a 25% uplift to reflect non-steady state emissions.
  Typical operating pressure 70psi (4 Barg)
    Site specific pressure may be difficult to determine

## Slide 17: AGI Venting – National Grid Estimate
 | Steady state venting rate (scf/m) | Specified operating pressure (psi) | Estimated mean NG operating pressure (psi) | Venting rate per device (scm/day) | Mean number of units on site | Annual venting rate (scm/yr) | Estimated 25% increase due to non steady state conditions (scm/yr/site)
Positioners | 0.2 | 20 | 70 | 28.8 | 5 | 52,560 | 65,700
Controllers | 0.05 | 20 | 70 | 7.2 | 9 | 23,652 | 29,565
 |  |  |  |  | Total | 76,212 | 95,265
LDZ | No. Sites | Estimated Venting (scm) |  | Impact |  |  | 
 |  | Proposed Model | Current Model | Volume (scm) | Energy | % | 
EA | 14 | 1,333,710 | 1,434,601 | -100,891 | -1 GWh | -7% | 
EM | 36 | 3,429,540 | 1,353,090 | 2,076,450 | 22 GWh | 153% | 
NT | 17 | 1,619,505 | 1,556,868 | 62,637 | 1 GWh | 4% | 
NW | 50 | 4,763,250 | 1,817,705 | 2,945,545 | 31 GWh | 162% | 
WM | 13 | 1,238,445 | 1,565,020 | -326,575 | -4 GWh | -21% | 
 | 130 | 12,384,450 | 7,727,284 | 4,657,166 | 49 GWh | 60% | 
Notes: Venting rates based on most common type – we are currently reviewing actual equipment on site
Operating pressure assumed to be 70psi (4 Barg); venting rate assumed to be linear with pressure
Assumed 25% uplift to account for non-steady state emissions

## Slide 18: AGI Venting - Summary
Original AGI venting estimate:
  Provenance?
  Fixed, therefore, no incentive to reduce
Proposal
  Site specific estimate
  Provides incentive to reduce venting
Issues
  Non-steady state venting difficult to estimate
    Should be included for completeness of Shrinkage estimate
    May be inappropriate to form part of an incentive

## Slide 19: Benefits of Proposals
Key criteria for the Leakage Model
  More Accurate
  More Robust
  Reflects Network specific data

## Slide 20: Next Steps - Consultation
Consult on changes – January/February 2012
  Any other changes?
  28 Day Consultation Period
Proposal needs to be independently assessed – February 2012
  GL Noble Denton were selected via a competitive tender for the previous modification

## Slide 21: Next Steps – Implementation Options
Implement in current Price Control Period
  Requirement to amend Environmental Emissions Baselines
  Changes applicable to 2011/12 and 2012/13 leakage assessments and Shrinkage calculations
Implement in RIIO GD1
  Baselines would include estimated impact of proposed modifications