## MER Register
Ref | Description | Offtake | Downstream Transporter | Significance | First Notified | Latest Update | Latest Error Status | Live/ Closed
EA001 | Error in orifice plate measurement | Great Wilbraham MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed | Status | Live/Closed
EA002 | Error in orifice plate measurement | Matching Green MTB | National Grid - DN | Low | 2009-09-07 | 2010-10-13 | No Rec Required | Closed | Error Notified | Live
EA003 | Error in orifice plate measurement | Peterborough Eye MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed | Invoiced | Closed
EA004 | Error in orifice plate measurement | Peterborough Eye MTB | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed | MER in Compilation | Live
EA005 | Error in orifice plate measurement | Roudham Heath MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed | MER in Published | Live
EA006 | Error in orifice plate measurement | West Winch MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed | No Rec Required | Closed
EA007 | Error in orifice plate measurement | Whitwell MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed | SMER in Compilation | Live
EA008 | Error in orifice plate measurement | Whitwell MTB | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed | SMER Published | Live
EA009 | Error in orifice plate measurement | Yelverton MTB | National Grid - DN | Low | 2010-04-06 | 2011-01-19 | Invoiced | Closed
EA010 | The tracker was upgraded to a chromatograph. | Royston | National Grid - DN | Low | 2011-06-01 | 2011-06-01 | Error Notified | Live
EM001 | Error in orifice plate measurement | Alrewas EM MTD | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
EM002 | Error in orifice plate measurement | Blaby MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
EM003 | Error in orifice plate measurement | Caldecott MTA | National Grid - DN | Low | 2009-09-07 | 2010-08-31 | SMER Published | Live
EM004 | Error in orifice plate measurement | Tur Langton MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
EM005 | Error in orifice plate measurement | Blyborough MTA | National Grid - DN | Low | 2010-04-06 | 2011-01-19 | Invoiced | Closed
NO001 | Bent orifice plate after impact from debri after high volume flows | Ganstead MTA | Northern Gas Networks - DN | Low | 2009-04-02 | 2009-11-23 | MER Published | Live
NO002 | Wrong K Factors entered in the Omni | Melkinthorpe MRA | Northern Gas Networks - DN | Low | 2009-07-07 | 2011-01-20 | Invoiced | Closed
NO003 | Turbine meter failure | Corbridge MRB | Northern Gas Networks - DN | Low | 2009-12-23 | 2009-12-24 | Error Notified | Live
NO004 | Turbine meter Failure | Tow Law MRA | Northern Gas Networks - DN | Low | 2010-04-21 | 2010-04-21 | Error Notified | Live
NO005 | Low DP Cell found out of tolerance | Elton MTA | Northern Gas Networks - DN | Low | 2010-06-11 | 2010-06-11 | Error Notified | Live
NO006 | Bishop Auckland AGI, Turbine meter flow computer operated with wrong set-up for approximately 57 minutes causing an under-registration of approximately 20% | Bishop Aukland MTA | Northern Gas Networks - DN | Low | 2010-05-19 | 2010-08-20 | MER in Compilation | Live
NO007 | Failure of Turbine HF | Asselby 7B MRA | Northern Gas Networks - DN | Low | 2010-07-27 | 2010-07-27 | Error Notified | Live
NO008 | Gas Passed through stream with spool piece unmetered | Baldersby MRB | Northern Gas Networks - DN | Low | 2010-12-22 | 2010-12-22 | Error Notified | Live
NO009 | Ruptured downstream pipework | Asselby 7B MRB | Northern Gas Networks - DN | Low | 2011-02-18 | 2011-02-18 | Error Notified | Live
NT001 | Error in orifice plate measurement | Horndon B MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NT002 | Error in orifice plate measurement | Luxborough Lane MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NT003 | Error in orifice plate measurement | Luxborough Lane MTB | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NT004 | Error in orifice plate measurement | Peters Green MTA | National Grid - DN | Medium | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NT005 | Error in orifice plate measurement | Peters Green MTB | National Grid - DN | Medium | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NT006 | Error in orifice plate measurement | Peters Green 2 (South Mimms) MTC | National Grid - DN | Medium | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NT007 | Error in orifice plate measurement | Peters Green 2 (South Mimms) MTD | National Grid - DN | Medium | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NT008 | The temperature sensor was reading about 5 degrees high. The error was caused by a bad connection between the sensor and the temperature transmitter. | Horndon B MTA | National Grid - DN | High | 2010-12-14 | 2010-12-14 | Error Notified | Live
NW001 | Error in orifice plate measurement | Blackrod MTA | National Grid - DN | High | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW002 | Error in orifice plate measurement | Blackrod MTB | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW003 | Error in orifice plate measurement | Ecclestone MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW004 | Error in orifice plate measurement | Holmes Chapel MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW005 | Error in orifice plate measurement | Mickle Trafford MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW006 | Error in orifice plate measurement | Samlesbury MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW007 | Error in orifice plate measurement | Warburton MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW008 | Error in orifice plate measurement | Weston Point MTB | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
NW009 | The orifice plate bore diameter was incorrectly measured. The incorrect bore was entered into the flow computer configuration without taking the drain hole into account. | Blackrod MTA | National Grid - DN | Low | 2009-10-08 | 2011-01-19 | Invoiced | Closed
SC001 | Incorrect K-factors entered in OMNI flow computer | Langholm MRA | Scotia Gas - DN | Low | 2008-12-01 | 2010-03-09 | Invoiced | Closed
SC002 | GAUGE PRESSURE TRANSMITTER ERROR | Lockerbie MTA | Scotia Gas - DN | Low | 2010-08-25 | 2010-08-31 | MER in Compilation | Live
SC003 | Calibration shift between calibrations | Langholm MRA | Scotia Gas - DN | Low | 2010-08-25 | 2010-08-31 | MER in Compilation | Live
SC004 | Failed ME2 Spin-Down Test. Report Will Be Forwarded To NG (UKT) As A 'Null Report' Hence No Entries In Flow Fields Below | Nether Howcleugh MRA | Scotia Gas - DN | Low | 2010-02-22 | 2010-02-22 | Error Notified | Live
SC005 | Faulty turbine meter wiring | Careston MRA | Scotia Gas - DN | Low | 2010-09-02 | 2010-09-02 | Error Notified | Live
SC006 | Incorrect orifice plate location in carrier | Aberdeen MTA | Scotia Gas - DN | High | 2010-09-24 | 2010-09-24 | Error Notified | Live
SC007 | LDP calibration error | Balgray MTA | Scotia Gas - DN | Low | 2010-12-23 | 2010-12-23 | Error Notified | Live
SC008 | Incorrect OMNI k-factor at one frequency point | Bathgate UMA | Scotia Gas - DN | Low | 2011-01-06 | 2011-01-06 | Error Notified | Live
SC009 | Turbine meter failure (single meter tube site). NULL report expected as Gas Control provided estimated DVOL's. | Careston MRA | Scotia Gas - DN | Low | 2011-01-17 | 2011-01-17 | Error Notified | Live
SE001 | Low dp cell output limited, preventing switchup to High cell | Tatsfield MTA | Scotia Gas - DN | Low | 2010-06-15 | 2010-03-09 | Invoiced | Closed
SE002 | Contamination on upstream face of orifice plate | Farningham MTA | Scotia Gas - DN | Low | 2009-09-21 | 2010-09-06 | MER Published | Live
SE003 | HIGH DP TRANSMITTER ERROR | Shorne MTA | Scotia Gas - DN | Low | 2010-08-31 | 2011-05-26 | MER in Compilation | Live
SE004 | Metering maximum exceeded for short duration (<5minutes) - NULL report expected | Farningham MTA | Scotia Gas - DN | Low | 2011-01-10 | 2011-01-10 | Error Notified | Live
SO001 | Equalising valve on Orifice Plate impulse lines to Differential pressure transmitters open. | Braishfield B MTB | Scotia Gas - DN | High | 2010-05-14 | 2010-08-31 | SMER in Compilation | Live
SO002 | Low dp transmitter error | Braishfield A MTA | Scotia Gas - DN | Low | 2010-08-25 | 2010-08-31 | Error Notified | Live
SO003 | Low dp and pressure transmitter errors | Braishfield B MTB | Scotia Gas - DN | Low | 2010-08-25 | 2010-08-31 | Error Notified | Live
SO004 | Low DP transmitter error | Braishfield A MTA | Scotia Gas - DN | Low | 2011-01-10 | 2011-01-10 | Error Notified | Live
SO005 | Errors on LDP, HDP, and Pressure transmitters | Braishfield B MTB | Scotia Gas - DN | Low | 2011-01-13 | 2011-01-13 | Error Notified | Live
SO006 | Error on HDP transmitter | Braishfield B MTB | Scotia Gas - DN | Low | 2011-01-14 | 2011-01-14 | Error Notified | Live
SO007 | HDP transmitter calibration error | Braishfield B MTB | Scotia Gas - DN | Low | 2011-01-20 | 2011-01-20 | Error Notified | Live
SW001 | Suspect Meter Fault. | Evesham MTA | Wales & West Utilities - DN | Medium | 2010-03-31 | 2009-12-07 | MER in Compilation | Live
SW002 | Pressure transducer locking up | Ilchester MTA | Wales & West Utilities - DN | Low | 2009-03-31 | 2010-09-22 | Invoiced | Closed
SW003 | Incorrect frequencies entered in Omni flow computer | Coffinswell MRA | Wales & West Utilities - DN | Low | 2009-07-08 | 2009-10-08 | No Rec Required | Closed
SW004 | Pressure transducer locking up | Seabank MTA | Wales & West Utilities - DN | Low | 2009-09-25 | 2010-09-22 | Invoiced | Closed
SW005 | Incorrect frequencies entered in Omni flow computer | Choakford MRA | Wales & West Utilities - DN | Low | 2009-10-27 | 2009-12-07 | No Rec Required | Closed
SW006 | Failed ADC checks | Evesham MTA | Wales & West Utilities - DN | Low | 2010-03-02 | 2010-05-18 | MER in Compilation | Live
SW007 | Incorrect K factors used in flow computer | Littleton Drew MRA | Wales & West Utilities - DN | Low | 2010-05-18 | 2011-04-15 | Invoiced | Closed
SW008 | Degradation of Turbine meter caused under registration of flow | Ross-On-Wye MRA | Wales & West Utilities - DN | Low | 2010-05-18 | 2011-01-21 | Invoiced | Closed
SW009 | Failed validation checks for pressure transmitter and temperature ADC | Ross-On-Wye MRB | Wales & West Utilities - DN | Low | 2010-05-18 | 2011-04-21 | Invoiced | Closed
SW010 | Loss of range due to software error | Aylesbeare MTA | Wales & West Utilities - DN | Low | 2010-05-26 | 2010-06-25 | MER in Compilation | Live
SW011 | Incorrect density figures calculated due to mismeasured composition figures by the chromatograph. | Ross-On-Wye MRB | Wales & West Utilities - DN | Low | 2010-09-13 | 2010-09-24 | MER in Compilation | Live
SW012 | Incorrect density figures calculated due to mismeasured composition figures by the chromatograph. | Ross-On-Wye MRB | Wales & West Utilities - DN | Low | 2010-09-13 | 2010-09-24 | MER in Compilation | Live
SW013 | Pressure transducer locking up | Evesham MTB | Wales & West Utilities - DN | Low | 2010-09-22 | 2010-10-05 | MER in Compilation | Live
SW014 | Calibration shift between calibrations | Ross-On-Wye MRA | Wales & West Utilities - DN | Medium | 2010-09-24 | 2011-04-21 | Invoiced | Closed
SW015 | Pressure transducer locked up. | Ilchester MTA | Wales & West Utilities - DN | Low | 2010-10-04 | 2010-10-05 | MER in Compilation | Live
SW016 | Pressure Transducer locking up | Aylesbeare MTA | Wales & West Utilities - DN | Low | 2010-10-25 | 2010-11-18 | MER in Compilation | Live
SW017 | Low Differential Pressure transmitter failed (AF) annual validation check | Easton Grey MTA | Wales & West Utilities - DN | Low | 2010-11-17 | 2010-11-18 | MER in Compilation | Live
SW018 | Faulty turbine meter wiring | Cirencester MRB | Wales & West Utilities - DN | Low | 2010-11-17 | 2010-11-17 | Error Notified | Live
SW019 | Lock up of metering pressure headcell | Ross WM MTA | Wales & West Utilities - DN | Low | 2010-12-23 | 2011-04-21 | Invoiced | Closed
SW020 | Pressure transducer locked up. | Aylesbeare MTA | Wales & West Utilities - DN | Low | 2011-04-18 | 2011-04-21 | MER in Compilation | Live
WM001 | Error in orifice plate measurement | Alrewas WM MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
WM002 | Error in orifice plate measurement | Alrewas WM MtB | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
WM003 | Error in orifice plate measurement | Audley (Dunkirk) MTE | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
WM004 | Error in orifice plate measurement | Austrey MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
WM005 | Error in orifice plate measurement | Ross WM MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
WM006 | Error in orifice plate measurement | Shustoke MTA | National Grid - DN | Low | 2009-09-07 | 2011-01-19 | Invoiced | Closed
WM007 | Error in orifice plate measurement | Hydes Pastures MTA | National Grid - DN | Low | 2009-10-08 | 2011-11-25 | SMER Published | Live
WM008 | Pressure transmitter locking up | Ross WM MTA | National Grid - DN | Low | 2009-10-19 | 2010-04-15 | Invoiced | Closed
WM009 | The chromatograph mismeasured the composition and an incorrect density was calculated. | Ross WM MTA | National Grid - DN | Low | not known | 2009-12-18 | MER in Compilation | Live
WM010 | The chromatograph mismeasured the composition and an incorrect density was calculated. | Ross WM MTA | National Grid - DN | Low | 2010-01-11 | 2010-01-11 | Error Notified | Live
WM011 | Failure of interposing volume integrator relay to telemetry resulting in under billing (MER/UKD/173/10) | Lower Quinton UMA & UMB | National Grid - DN | Low | 2010-12-21 | 2010-12-21 | Error Notified | Live
WM012 | As a result of the failure of the autochangover system, the second cylinder of helium carrier gas was not brought on line. This depleted the first cylinder beyond that which could support the chromatograph. | Rugby MTA | National Grid - DN | Low | 2011-03-02 | 2011-03-02 | Error Notified | Live
WS001 | Intermittent fault with Pressure Transmitter | Gilwern MTA | Wales & West Utilities - DN | Medium | 2009-03-31 | 2010-09-28 | Invoiced | Closed
WN001 | Incorrect density figures calculated due to mismeasured composition figures by the chromatograph. | Maelor MUB | Wales & West Utilities - DN | Low | 2011-07-01 | 2011-07-01 | Error Notified | Live

## Offtake Data
Look Up Table For Offtake Data
DN/NTS Offtake Meter | Site Type | Short Code | Upstream Transporter | Downstream Transporter | LDZ | Meter Type
Aberdeen MTA | Offtake | ABEROF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Alrewas EM MTD | Offtake | ALREOF | National Grid - NTS | National Grid - DN | EM | Orifice
Alrewas WM MTA | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Alrewas WM MTB | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Armadale MTA | Offtake | ARMAOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Aspley MTA | Offtake | ASPYOF | National Grid - NTS | National Grid - DN | WM | Orifice
Asselby 38B MRC | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Asselby 38B MRD | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRA | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRB | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Atherstone MRA | Inter LDZ Offtake | <none> | National Grid - DN | National Grid - DN | WM | Turbine
Atherstone MRB | Inter LDZ Offtake | <none> | National Grid - DN | National Grid - DN | WM | Turbine
Audley (Crewe) MTC | Offtake | AUDNOF | National Grid - NTS | National Grid - DN | NW | Orifice
Audley (Dunkirk) MTD | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Audley (Dunkirk) MTE | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Austrey MTA | Offtake | AUSTOF | National Grid - NTS | National Grid - DN | WM | Orifice
Aylesbeare MTA | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Bacton MRD | Offtake | BADSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Baldersby MRA | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Baldersby MRB | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Balgray MTA | Offtake | BALGOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Bathgate UMA | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bathgate UMB | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bishop Aukland MTA | Offtake | BISHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Blaby MTA | Offtake | BLABOF | National Grid - NTS | National Grid - DN | EM | Orifice
Blackrod MTA | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blackrod MTB | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blyborough MTA | Offtake | BLYBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Bracknell MTA | Inter LDZ Offtake | <none> | Scotia Gas - DN | National Grid - DN | NT | Orifice
Braishfield A MTA | Offtake | BRAAOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Braishfield B MTB | Offtake | BRABOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Brisley MRA | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Brisley MRB | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Broxburn MTA | Offtake | BROXOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Burley Bank MTA | Offtake | BURLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Caldecott MRB | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Turbine
Caldecott MTA | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Orifice
Careston MRA | Offtake | CAREOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Choakford MRA | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Choakford MRB | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRB | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRB | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRA | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coldstream MTA | Offtake | COLDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Corbridge MRA | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Corbridge MRB | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Cowpen Bewley MTA | Offtake | COWPOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Dowlais MTA | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Dowlais MTB | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Drointon UMA | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drointon UMB | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drum MTA | Offtake | DRUMOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Dunstall Green MRA | Inter LDZ Offtake | <none> | Scotia Gas - DN | National Grid - DN | NT | Turbine
Dyffryn Cladach MTA | Offtake | DYFNOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Easton Grey MTA | Offtake | EGRYOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ecclestone MTA | Offtake | ECCLOF | National Grid - NTS | National Grid - DN | NW | Orifice
Elton MTA | Offtake | ELTNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Evesham MTA | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Evesham MTB | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Farningham MTA | Offtake | FARNOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Fiddington MTA | Offtake | FIDDOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ganstead MTA | Offtake | GANSOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Gilwern MTA | Offtake | GILWOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Glenmavis MTA | Offtake | GLENOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Glenmavis MTC | Offtake | GLENOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Gosberton MTA | Offtake | GOSBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Great Wilbraham MTA | Offtake | GWILOF | National Grid - NTS | National Grid - DN | EA | Orifice
Guyzance MRA | Offtake | GUYZOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Guyzance MRB | Offtake | GUYZOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Hardwick | Offtake | HARDOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Holmes Chapel MTA | Offtake | HOLMOF | National Grid - NTS | National Grid - DN | NW | Orifice
Horndon B MTA | Offtake | HORNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Humbleton MRA | Offtake | HUMBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Humbleton MRB | Offtake | HUMBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Hume MRA | Offtake | HUMEOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Hume MRB | Offtake | HUMEOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Hydes Pastures MTA | Inter LDZ Offtake | <none> | National Grid - DN | National Grid - DN | WM | Orifice
Ilchester MTA | Offtake | ILCHOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ipsden MTA | Offtake | IPDNOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Keld MRA | Offtake | KELDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Kenn MTA | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kenn MTB | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kinknockie MRA | Offtake | KINKOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Kinknockie MRB | Offtake | KINKOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Kirkstead MRB | Offtake | KIRKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Kirkstead MTA | Offtake | KIRKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Langholm MRA | Offtake | LANGOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Leamington MRA | Offtake | LEAMOF | National Grid - NTS | National Grid - DN | WM | Turbine
Leamington MRB | Offtake | LEAMOF | National Grid - NTS | National Grid - DN | WM | Turbine
Little Burdon MTA | Offtake | LBUROF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Littleton Drew MRA | Offtake | LTDWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Lockerbie MTA | Offtake | LOCKOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Lower Quinton UMA | Offtake | LOWQOF | National Grid - NTS | National Grid - DN | WM | Ultrasonic
Lower Quinton UMB | Offtake | LOWQOF | National Grid - NTS | National Grid - DN | WM | Ultrasonic
Lupton MTA | Offtake | LUPTOF | National Grid - NTS | National Grid - DN | NW | Orifice
Luxborough Lane MTA | Offtake | LUXBOF | National Grid - NTS | National Grid - DN | NT | Orifice
Luxborough Lane MTB | Offtake | LUXBOF | National Grid - NTS | National Grid - DN | NT | Orifice
Maelor MTA | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Orifice
Maelor MTB | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Turbine
Malpas MRA | Offtake | MALPOF | National Grid - NTS | National Grid - DN | NW | Turbine
Mappowder MTA | Offtake | MAPPOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Market Harborough MTA | Offtake | MKHBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Matching Green MTA | Offtake | MTCHOF | National Grid - NTS | National Grid - DN | EA | Orifice
Matching Green MTB | Offtake | MTCHOF | National Grid - NTS | National Grid - DN | EA | Orifice
Melkinthorpe MRA | Offtake | MELKOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Mickle Trafford MTA | Offtake | MICKOF | National Grid - NTS | National Grid - DN | NW | Orifice
Milwich MTA | Offtake | MILWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Nether Howcleugh MRA | Offtake | NETHOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Nether Howcleugh MRB | Offtake | NETHOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pannal MTA | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Pannal MTB | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Partington MTA | Offtake | PART OF | National Grid - NTS | National Grid - DN | NW | Orifice
Paull MTA | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Paull MTB | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Peterborough Eye MTA | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peterborough Eye MTB | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peters Green 2 (South Mimms) MTC | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 2 (South Mimms) MTD | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green MTA | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green MTB | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Pickering MTA | Offtake | PICKOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Pitcairngreen MRA | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pitcairngreen MRB | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pucklechurch MTA | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Rawcliffe MRA | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Rawcliffe MRB | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Ross WM MTA | Offtake | ROSSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Ross-On-Wye MRA | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Ross-On-Wye MRB | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Roudham Heath MTA | Offtake | ROUDOF | National Grid - NTS | National Grid - DN | EA | Orifice
Royston MRA | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Royston MRB | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Rugby MTA | Offtake | RUGBOF | National Grid - NTS | National Grid - DN | WM | Orifice
Saltwick 1 | Offtake | SALTOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Samlesbury MTA | Offtake | SAMLOF | National Grid - NTS | National Grid - DN | NW | Orifice
Seabank MTA | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Shorne MTA | Offtake | SHOROF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Shustoke MTA | Offtake | SHUSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Silk Willoughby MRA | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Silk Willoughby MRB | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Soutra MTA | Offtake | SOUTOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
St Fergus MTA | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
St Fergus MTB | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRA | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRB | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stratford MRA | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Stratford MRB | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Sutton Bridge MRA | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Sutton Bridge MRB | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Tatsfield MTA | Offtake | TATSOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Thornton Curtis MTA | Offtake | CURTOF | National Grid - NTS | National Grid - DN | EM | Orifice
Thrintoft MTA | Offtake | THRNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Tow Law MRA | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Tow Law MRB | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Towton MTA | Offtake | TOWTOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Tur Langton MTA | Offtake | TURLOF | National Grid - NTS | National Grid - DN | EM | Orifice
Walesby MRA | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Walesby MRB | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Warburton MTA | Offtake | WARBOF | National Grid - NTS | National Grid - DN | NW | Orifice
West Winch MTA | Offtake | WINCOF | National Grid - NTS | National Grid - DN | EA | Orifice
Weston Point MTB | Offtake | WESTOF | National Grid - NTS | National Grid - DN | NW | Orifice
Wetheral MTA | Offtake | WETHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Whitwell MTA | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Whitwell MTB | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Winkfield 2 MTB | Offtake | WNKSOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Winkfield MTA | Offtake | WINKOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Winkfield NT MTC | Offtake | WINTOF | National Grid - NTS | National Grid - DN | NT | Orifice
Yelverton MTB | Offtake | YELVOF | National Grid - NTS | National Grid - DN | EA | Orifice
Systematic Bias | Over/Under Indicator | Error Magnitude |  | Error Status
Yes | Over | High | >= 50 GWh | Error Notified
No | Under | Low | < 30 GWh | MER in Compilation
|  | Medium | >= 30, < 50 GWh | SMER in Compilation
MER Published
SMER Published
Awaiting First Available Invoice
Invoiced
Closed / No Rec Required