## General
CAT | 3 - GENERAL
DATE
SITE NAME
| SITE DESCRIPTION | Official | Orifice | 2 Stream
O | Any obvious signs of gas leakage? |  | Events outside, on site, are coloured blue
A | Is the Bypass stream isolated?
D | Ofgem seal intact?
O | Ofgem sealed valve number
B | Site validated within required timescale |  | Sites should be validated annually with a maximum interval of eighteen months between validations.
| Date of last validation |  | HPMIS Site validation records
B | Validation carried out over the period |  | Previous validation
COMMENT
4 - PRE/POST FLOW CHECK
| Is the site pressure or volume controlled? |  | This refers to the type of Flow Control in operation on the Site
Does the system operator accept the results?
| Local checks (if relevant) | Pre | Post | Parameters from the Telemetry Local Display Unit
| FCV/PCV |  |  | %
| F1 |  |  | mscm/d
| P1 |  |  | barg
| P5 |  |  | barg
INTG (Integrator Volume)
| METER_1_DP |  |  | mbar
COMMENT
5 - LOG BOOKS & DOCUMENTATION
O | Copy of current maintenance procedures available on site?
B | Confirm status of the calibration/validation results? |  | Page 8 ME2 summary sheet (CP16)
O | Metering log satisfactory? |  | View entries in Ofgem Log
O | Flow computer backup configuration available on site? |  | Saved on Allen Bradley - Apps>OMNI> Folder
COMMENT
| NAME OF EXAMINER |  | DATE
| David Whitelaw |  | 0
NAME OF SITE REPRESENTATIVE
Meter Inspection Categories
Category A
A non-conformance which indicates that the system is not complying with the criteria, and which has led, or is likely to lead, to a mis-measurement, which will require correction.
Category B
Insufficient information available at the time of the metering inspection to determine whether a non-conformance has occurred.
Category C
A non-conformance which may indicate that the system is not being operated or maintained correctly or procedure not being followed, which has neither led to, nor is likely to lead to a
mis-measurement
Category D
A non-conformance, which indicates that the system has not been complying with the criteria. The non-conformance no longer exists, but may require correction of data or calculations.
Category O
Observations: A finding on site that does not fit into any category but is worthy of note.
T/PR/ME/2 Part 3: 8. General Requirements - states all sites must be validated with a maximum interval of eighteen months between validations.
The validation of a site must be completed within one month of commencement
1. Every 12mths offtake metering should be validated
2. Allowing for operational workload etc. the validation may exceed the 12 mth date up to 6mths after the due date.
3. Validations completed which were overdue by up to 6 mths still require a follow up validation 12 mths from the original due date.
4. Over along term e.g. 5 years. 5 validations will have been completed each due 12 mths from the original date due, and each one never exceeding 18 mths from the previous.

## Primary meter 1
CAT | 6 - PRIMARY METER(1)
| SITE NAME | 0 |  |  | 0
| SITE DESCRIPTION | Official | Orifice
O | Meter reference |  |  | e.g. MTA, MRB
O | OMNI stream number?
| 6.1 ORIFICE METER TUBE |  |  | Data from Meter Tube certificates / Meter Tube plate
B | Meter Tube Identifier
B | Tube internal diameter | Certified |  | mm
AB |  | Applied
B | Tube Calibration temperature | Certified |  | deg.C
AB |  | Applied
AB | Tube expansion temperature coefficient | Declared |  | deg.C | Omnicom meter run setup
AB |  | Applied
The figures in the OMNI are values for the materials used - typically carbon steel for the meter tubes which has a tube expansion temperature coeff. of 0.0000112mm/m/degC.
These values can be verified against material specifications or AGA3.
Comment
6.2 ORIFICE PLATE
O | Serial Number
O | Verify against metering log
A | Orifice diameter | Certified |  | mm
A |  | Applied
A | Orifice calibration temperature | Certified |  | deg.C
A |  | Applied
AB | Plate expansion temperature coefficient | Declared |  | deg.C | Omnicom meter run setup
AB |  | Applied
The figures in the OMNI are values for the materials used, typically 304 & 316 stainless steel for the orifice plates which has an expansion temperature coeff. of 0.0000167mm/m/degC
A | Calibration authority and accreditation
Certificate No.
Calibration date
Installation date
Is there a drain hole?
A | Drain hole dimensions taken into account?
B | Changed at required frequency? |  |  | Annually
COMMENT
| 7 - TURBINE METER |  |  | Data from Turbine meter calibration certificate
B | Meter Identifier
A | Verify against certificate?
O | Verify against log?
A | Calibration authority and accreditation (high pressure Natural gas)
Certificate No.
Calibration date (high pressure Natural gas)
B | Inspection carried out at required frequency? |  |  | 12 months
Is the meter a lubricated type?
A | Spin down test performed?
| Spin down times |  |  | seconds
| Frequency/K-factor pairs traceable back to the linearisation spreadsheet and then back to meter high-pressure calibration certificate |  | Frequency (Hz) |  | K-factor (pulses/cu.m)
|  |  | Declared | Applied | Declared | Applied
A
B | Calibration carried out every 8 years? (Non-Lubricated)
Comment
| 8 - USM |  |  | Data from USM calibration certificates
B | Meter Identifier
A | Verify against certificate?
O | Verify against log?
Calibration date (high pressure Natural gas)
A | Calibration authority (high pressure Natural gas)
| Frequency/K-factor pairs traceable back to the linearisation spreadsheet and then back to meter high-pressure calibration certificate |  | Frequency (Hz) |  | K-factor (pulses/cu.m)
|  |  | Declared | Applied | Declared | Applied
A
O | Calibration carried out at required frequency? |  |  | The accepted interval for re-calibration of an Ultrasonic Meter is 8 years, please record last calibration date
B | Meter tube diameter (Instromet meter only) |  |  | mm
Comment
| NAME OF EXAMINER |  | DATE
| David Whitelaw |  | 0
NAME OF SITE REPRESENTATIVE
0

## Primary meter 2
CAT | 6 - PRIMARY METER(2)
| SITE NAME | 0 |  |  | 0
| SITE DESCRIPTION | Official | Orifice
O | Meter reference |  |  | e.g. MTA, MRB
O | OMNI stream number?
| 6.1 ORIFICE METER TUBE |  |  | Data from Meter Tube certificates / Meter Tube plate
B | Meter Tube Identifier
B | Tube internal diameter | Certified |  | mm
AB |  | Applied
B | Tube Calibration temperature | Certified |  | deg.C
AB |  | Applied
AB | Tube expansion temperature coefficient | Declared |  | deg.C | Omnicom meter run setup
AB |  | Applied
The figures in the OMNI are values for the materials used - typically carbon steel for the meter tubes which has a tube expansion temperature coeff. of 0.0000112mm/m/degC.
These values can be verified against material specifications or AGA3.
Comment
6.2 ORIFICE PLATE
O | Serial Number
O | Verify against metering log
A | Orifice diameter | Certified |  | mm
A |  | Applied
A | Orifice calibration temperature | Certified |  | deg.C
A |  | Applied
AB | Plate expansion temperature coefficient | Declared |  | deg.C | Omnicom meter run setup
AB |  | Applied
The figures in the OMNI are values for the materials used, typically 304 & 316 stainless steel for the orifice plates which has an expansion temperature coeff. of 0.0000167mm/m/degC
A | Calibration authority and accreditation
Certificate No.
Calibration date
Installation date
Is there a drain hole?
A | Drain hole dimensions taken into account?
B | Changed at required frequency? |  |  | Annually
COMMENT
| 7 - TURBINE METER |  |  | Data from Turbine meter calibration certificate
B | Meter Identifier
A | Verify against certificate?
O | Verify against log?
A | Calibration authority and accreditation (high pressure Natural gas)
Certificate No.
Calibration date (high pressure Natural gas)
B | Inspection carried out at required frequency? |  |  | 12 months
Is the meter a lubricated type?
A | Spin down test performed?
| Spin down times |  |  | seconds
| Frequency/K-factor pairs traceable back to the linearisation spreadsheet and then back to meter high-pressure calibration certificate |  | Frequency (Hz) |  | K-factor (pulses/cu.m)
|  |  | Declared | Applied | Declared | Applied
A
B | Calibration carried out every 8 years? (Non-Lubricated)
Comment
| 8 - USM |  |  | Data from USM calibration certificates
B | Meter Identifier
A | Verify against certificate?
O | Verify against log?
Calibration date (high pressure Natural gas)
A | Calibration authority (high pressure Natural gas)
| Frequency/K-factor pairs traceable back to the linearisation spreadsheet and then back to meter high-pressure calibration certificate |  | Frequency (Hz) |  | K-factor (pulses/cu.m)
|  |  | Declared | Applied | Declared | Applied
A
O | Calibration carried out at required frequency? |  |  | The accepted interval for re-calibration of an Ultrasonic Meter is 8 years, please record last calibration date
B | Meter tube diameter (Instromet meter only) |  |  | mm
Comment
| NAME OF EXAMINER |  | DATE
| David Whitelaw |  | 0
NAME OF SITE REPRESENTATIVE
0

## Secondary Instr 1
CAT | 9 - 12 Secondary Instrumentation(1)
| SITE NAME | 0 |  |  | 0
| SITE DESCRIPTION | Official | Orifice
9 DIFFERENTIAL PRESSURE TRANSMITTERS
|  |  | Low DP | High DP | Standby DP
O | TAG
B | Transmitter identifier
A | Calibrated range | Calibrated HPMIS |  |  |  | mbar
A |  | Applied OMNI
O | Verify against metering log
B | Validated at required frequency? |  |  |  |  | 12 months
A | DWT manufacturers Calibration temperature applied in accordance with Network procedure |  |  | GMR 68 HPMIS
A | Local gravity correction factor applied in accordance with Network procedure |  |  | HPMIS
B | Zero check at high static pressure? |  |  | CP11 | static pressure zero | HPMIS
COMMENT
10 PRESSURE TRANSMITTER
O | TAG
B | Transmitter identifier
A | Calibrated range | Calibrated |  | barg | HPMIS
A |  | Applied
O | Verify against Metering log? |  |  | HPMIS
B | Validated at required frequency? |  |  | HPMIS
A | DWT manufacturers Calibration temperature applied in accordance with Network procedure |  |  | HPMIS
A | Local gravity correction factor applied in accordance with Network procedure
B | Local gravity correction factor | Certified
A |  | Applied
COMMENT
11 EQUALISATION VALVES AND IMPULSE LINES FOR DP AND P TRANSMITTERS
Condition of impulse lines
B | Impulse lines fall to tapping points?
B | Any low points in impulse lines without drain-legs?
A | Position of pressure measurement point correct? |  |  | Orifice plates: high side of the diff. pressure.
Turbine and USM's on the body of the meter.
COMMENT
12 TEMPERATURE TRANSMITTER/TRANSDUCER
O | TAG
Is a 4-20mA transmitter fitted?
Type of Sensor - Thermowell OR Surface Mounted
Installations with surface mount temperature probes - record the insulation details
of the sensor on the pipe, ie type of insulation, depth and distance each side. If no
insulation, request that the operator demonstrates the measurement uncertainty is achieved.
A | Calibrated range | Calibrated |  | degC | HPMIS
A |  | Applied
A | Position of measurement point correct? For orifice-plates, using a thermowell, |  |  | this is between 5D and 15D downstream.
Turbine meters using a thermowell, this is within 5D downstream. Ultrasonic meters this is between 2D and 5D downstream.
If a surface mounted sensor is used, then the position for all types of meter can be upstream OR downstream - within 5D.
O | Verify against Metering log? HPMIS
B | Validated at required frequency? HPMIS
COMMENT
| NAME OF EXAMINER |  | DATE
| David Whitelaw |  | 0
NAME OF SITE REPRESENTATIVE
0

## Secondary Instr 2
CAT | 9 - 12 Secondary Instrumentation(2)
| SITE NAME | 0 |  |  | 0
| SITE DESCRIPTION | Official | Orifice
9 DIFFERENTIAL PRESSURE TRANSMITTERS
|  |  | Low DP | High DP | Standby DP
O | TAG
B | Transmitter identifier
A | Calibrated range | Calibrated HPMIS |  |  |  | mbar
A |  | Applied OMNI
O | Verify against metering log
B | Validated at required frequency? |  |  |  |  | 12 months
A | DWT manufacturers Calibration temperature applied in accordance with Network procedure |  |  | GMR 68 HPMIS
A | Local gravity correction factor applied in accordance with Network procedure |  |  | HPMIS
B | Zero check at high static pressure? |  |  | static pressure zero | HPMIS
COMMENT
10 PRESSURE TRANSMITTER
O | TAG
B | Transmitter identifier
A | Calibrated range | Calibrated |  | barg | HPMIS
A |  | Applied
O | Verify against Metering log? |  |  | HPMIS
B | Validated at required frequency? |  |  | HPMIS
A | DWT manufacturers Calibration temperature applied in accordance with Network procedure |  |  | HPMIS
A | Local gravity correction factor applied in accordance with Network procedure
B | Local gravity correction factor | Certified
A |  | Applied
COMMENT
11 EQUALISATION VALVES AND IMPULSE LINES FOR DP AND P TRANSMITTERS
Condition of impulse lines
B | Impulse lines fall to tapping points?
B | Any low points in impulse lines without drain-legs?
A | Position of pressure measurement point correct? |  |  | Orifice plates: high side of the diff. pressure.
Turbine and USM's on the body of the meter.
COMMENT
12 TEMPERATURE TRANSMITTER/TRANSDUCER
O | TAG
Is a 4-20mA transmitter fitted?
Type of Sensor - Thermowell OR Surface Mounted
Installations with surface mount temperature probes - record the insulation details
of the sensor on the pipe, ie type of insulation, depth and distance each side. If no
insulation, request that the operator demonstrates the measurement uncertainty is achieved.
A | Calibrated range | Calibrated |  | degC | HPMIS
A |  | Applied
A | Position of measurement point correct? For orifice-plates, using a thermowell, |  |  | this is between 5D and 15D downstream.
Turbine meters using a thermowell, this is within 5D downstream. Ultrasonic meters this is between 2D and 5D downstream.
If a surface mounted sensor is used, then the position for all types of meter can be upstream OR downstream - within 5D.
O | Verify against Metering log? HPMIS
B | Validated at required frequency? HPMIS
COMMENT
| NAME OF EXAMINER |  | DATE
| David Whitelaw |  | 0
NAME OF SITE REPRESENTATIVE
0

## Flow computer
CAT | 13 - 15 Flow Computer Gas Properties & Odorisation
| SITE NAME | 0 |  |  | 0
| SITE DESCRIPTION | Official | Orifice
Below relate to the last backed up config file in the Omni.
| 13 FLOW COMPUTER | STREAM 1 | STREAM2
B | Temperature: Override code = 3? ('Average on fail') |  |  |  | Temperature setup
B | Pressure: Override code = 3? ('Average on fail') |  |  |  | Pressure setup
B | Diff Pressure: Override code = 3? ('Average on fail') DPLR Low |  |  |  | Diff. pressure setup
B | Diff Pressure: Override code = 3? ('Average on fail') DPHR High
B | Diff Pressure: Override code = 3? ('Average on fail') DPST Standby |  |  |  | Stream 1 in stream 3. Stream 2 in stream 4 for standby (GMR 5)
A | Atmospheric Pressure = 1.01325 bara? (Metric Standard Conditions) |  |  |  | Factor setup
A | Base Pressure = 1.01325 bara?
A | Base Temperature = 15 deg.C?
A | Density of Air = 1.22541 kg/m3?
| Value for Viscosity |  |  |  | Fluid data analysis
Value for Isentropic index
B | Source of values for Viscosity & Isentropic Index |  |  |  | updated annually - Metering Manager, or live values (UKD)
Analyser Site
A | Density Method: Code = 1? ('AGA-8 1994 Detailed Characterisation') |  |  |  | Fluid data analysis
Tracker Site
A | Density Method: Code = 2? ('AGA-8 1994 Gross Characterisation') |  |  |  | Fluid data analysis
B | Heating Value Method: Code = 2? ('ISO 6976')
A | Configuration OK? (CP9) |  |  |  | HPMIS
A | O/P Upstream temperature measurement: setup = 'N' Downstream or 'Y' upstream |  |  | Meter run setup (0=N, 1=Y)
A | O/P Downstream pressure measurement: Code = 0? ('NO') |  |  | Meter run setup (0=N, 1=Y)
O | Meter Suspect Alarm clear? |  |  |  | Red LED on omni front panel or LDU location
COMMENT:
| 14 GAS PROPERTIES | DANVIEW Screen | Omni (live rdgs) Fluid data analysis
|  | Chromatograph | Flow Computer
O | Methane |  |  | %
O | CV |  |  | MJ/m3
O | RD
either or
|  | Tracker | Flow Computer
O | CO2 |  |  | % | To agree with metering managers instruction
O | CV |  |  | MJ/m3
O | RD |  |  |  | To agree with metering managers instruction
B | Gas properties check OK? (CP8a/b) |  |  | HPMIS
COMMENT
15 ODORISATION
Is the odorisation system operating?
O | Odorant and flow computer displayed flowrates match? |  | Tol. +/- 1 % (Compare OMNI Flow readout with SCIM panel readout -relative)
COMMENT:
| NAME OF EXAMINER |  | DATE
| David Whitelaw |  | 0
NAME OF SITE REPRESENTATIVE
0

## Issues
SITE
0
Official
Orifice
2 Stream
Gas Examiner
David Whitelaw
GDN representative
0
Date
0 | Issues/Comments
GENERAL | 0
PRE/POST FLOW CHECK | 0
LOG BOOKS & DOCUMENTATION | 0
ORIFICE METER TUBE S1 | 0
PRIMARY METER 1 O/P | 0
PRIMARY METER 1 TURBINE | 0
PRIMARY METER 1 USM | 0
ORIFICE METER TUBE S2 | 0
PRIMARY METER 2 O/P | 0
PRIMARY METER 2 TURBINE | 0
PRIMARY METER 2 USM | 0
DIFFERENTIAL PRESSURE TRANSMITTERS S1 | 0
10 PRESSURE TRANSMITTER S1 | 0
IMPULSE LINES & POSITION OF PT S1 | 0
TEMPERATURE TRANSMITTER/TRANSDUCER S1 | 0
DIFFERENTIAL PRESSURE TRANSMITTERS S2 | 0
PRESSURE TRANSMITTER S2 | 0
IMPULSE LINES & POSITION OF PT S2 | 0
TEMPERATURE TRANSMITTER/TRANSDUCER S2 | 0
FLOW COMPUTER | 0
GAS PROPERTIES | 0
ODORISATION | 0

## Outside sheet
Date:
Site:
Any obvious signs of gas leakage?
Is the Bypass stream isolated?
Ofgem seal intact?
Ofgem sealed valve number
6.1 ORIFICE METER TUBE
Meter Tube Identifier
7 - TURBINE METER
Meter Identifier
8 - USM
Meter Identifier
O/P's only
9 DIFFERENTIAL PRESSURE TRANSMITTERS | Low DP | High DP | Standby DP
TAG
Transmitter identifier
10 PRESSURE TRANSMITTER
TAG
Transmitter identifier
Position of pressure measurement point correct? |  | O/P's: high side of the diff. pressure.
Turbine and USM's on the body of the meter.
11 EQUALISATION VALVES AND IMPULSE LINES FOR DP AND P TRANSMITTERS
Condition of impulse lines
Impulse lines fall to tapping points?
Any low points in impulse lines without drain-legs?
12 TEMPERATURE TRANSMITTER/TRANSDUCER |  | If a surface mounted sensor is used then for all types
TAG |  | of meter it can be upstream OR downstream within 5D
O/P's between 5D & 15D d/stream.
Position of measurement point correct? |  | Turbine meters within 5D d/stream;
Ultrasonic meters between 2D and 5D d/stream.
15 ODORISATION
Is the odorisation system operating?
Date:
Site:
Any obvious signs of gas leakage?
Is the Bypass stream isolated?
Ofgem seal intact?
Ofgem sealed valve number
6.1 ORIFICE METER TUBE
Meter Tube Identifier
7 - TURBINE METER
Meter Identifier
8 - USM
Meter Identifier
O/P's only
9 DIFFERENTIAL PRESSURE TRANSMITTERS | Low DP | High DP | Standby DP
TAG
Transmitter identifier
10 PRESSURE TRANSMITTER
TAG
Transmitter identifier
Position of pressure measurement point correct? |  | O/P's: high side of the diff. pressure.
Turbine and USM's on the body of the meter.
11 EQUALISATION VALVES AND IMPULSE LINES FOR DP AND P TRANSMITTERS
Condition of impulse lines
Impulse lines fall to tapping points?
Any low points in impulse lines without drain-legs?
12 TEMPERATURE TRANSMITTER/TRANSDUCER |  | If a surface mounted sensor is used then for all types
TAG |  | of meter it can be upstream OR downstream within 5D
Position of measurement point correct? |  | O/P's between 5D & 15D d/stream.
Turbine meters within 5D d/stream;
Ultrasonic meters between 2D and 5D d/stream.
15 ODORISATION
Is the odorisation system operating?