## Slide 1: Gas Energy Measurement in Consumer Billing
Presentation to UNC Workgroup 0693R
25/02/2020

## Slide 2: Overview
Background
  Request by Ofgem
  Two studies undertaken – different, but related
Approach taken
Key results
Implications for shrinkage

## Slide 3: Background
In January 2014, Ofgem requested technical support in two areas:
  Accuracy of thermal energy determined within the Gas (Calculation of Thermal Energy) Regulations and the impact on domestic gas consumers
  Assessing the consumer impact of relaxation in accuracy of CV determination devices used to determine the CV of biomethane injected into gas distribution systems
Two different studies, but
  Both related
  Both may have significance in shrinkage calculations
Report was published on Ofgem’s website
  Follow-up discussions between Ofgem and another party

## Slide 4: Approach taken
Accuracy of consumer billing
  Mathematical model of consumer billing
  Estimate the error in energy determined for three groups of consumers on each day of 2011:
    GB as a whole
    The 13 charging zones/LDZs
    The 2564 GB outcodes
  Output from the model:
    365 estimates of error in daily energy for each of the three groups
    Uncertainty in each estimate of daily energy

## Slide 5: Approach taken
Accuracy of biomethane CVDDs
  Mathematical model of daily charging area CV (FWACV)calculation
  Estimation the uncertainty in the daily charging area CV
  Output from the model:
    FWACV and uncertainty in FWACV for all LDZs for each day in 2011
    Explored impact of biomethane flows whose energy wa determined with CVDDs of varying accuracy

## Slide 6: Results
Accuracy of consumer billing study
  GB as a whole, mean error in annual energy during 2011
  GB as a whole, mean error in daily energy during 2011

## Slide 7: Results
Accuracy of consumer billing study
  GB as a whole, mean error in annual energy during 2011
  GB as a whole, mean error in daily energy during 2011
This represents variation in geographical and meteorological factors seen across GB

## Slide 8: Results
Accuracy of consumer billing study
  GB as a whole, mean error in annual energy during 2011
  GB as a whole, mean error in daily energy during 2011
Mean error in annual energy is reduced because individual daily errors tend to be negative during Autumn/Winter (when gas consumption is higher) and positive duing Spring/Summer (when gas consumption is lower).

## Slide 9: Results
Accuracy of consumer billing study
  GB as a whole, mean error in annual energy during 2011
  GB as a whole, mean error in daily energy during 2011
Uncertainty in error in annual energy is reduced because seasonal variation is removed.

## Slide 10: Dominated by distribution in errors

## Slide 11: Temperature and pressure dominate

## Slide 12: Results
Accuracy of consumer billing study
  Use of a single fixed factor necessarily results in over-/under-billing of groups of consumers
  Outcode level:
  Use of alternative fixed factors would have corrected the mean error, but at the expense of increased over-billing
  Use of LDZ-specific fixed factors would have reduced the width of the distribution of errors in energy, but largely by reducing under-billing (over-billing largely unchanged)
  Some benefit from incorporating mean height at each outcode

## Slide 13: Results
Accuracy of biomethane CVDDs study
  Expanded uncertainty in daily charging area CV estimated to be around
  (or 0.2%)
  Because biomethane sites are expected to be a relatively small proportion of daily energy, the impact of accuracy in their determined daily energies is relatively minor
  Values for maximum permissible errors suggested for different threshold flows
  Applicable to any gas, not just biomethane

## Slide 14: Implications for shrinkage
Accuracy of consumer billing
  UIG = energy output – energy input
  Errors in energy output contribute to error in UIG (same sign)
Accuracy of energy input metering
  Errors in energy inputs also contribute to error in UIG
  Are input errors significant?
  Estimates of uncertainty in determined UIG?
Shippers’ portfolios are another group of consumers
  Distribution in geography and meteorological factors
  Large portfolios might be expected to even out