## Notification Sheet
Measurement Error Notification
Unique Reference Number (Allocated by Joint Office) |  | EA019
DN Reference | MER/CAD/226/22
Error Status | Closed / No Rec Required
Brief Description | The incorrect orifice plate calibration reference temperature was entered into the Omni flow computer due to ambiguity between the environment temperature and the orifice plate surface temperature on the calibration certificate. The error is approximately -0.001217% which is approximately 100 times smaller than the 0.1% of daily flow required for a reconcilable MER.
Reason Measurement Error Detected | The error was discovered by SGS after reviewing data collected during a site visit.
Process Dates | Latest Notification Update | 2022-12-29 | dd/mm/yyyy
| Anticipated MER/SMER Publication | 2022-12-29 | dd/mm/yyyy
Measurement Error Dates | Discovered | 2022-11-18 | dd/mm/yyyy
| First Notified | 2022-12-29 | dd/mm/yyyy
| First Gas Day Where Error Present*1 or; | 2022-07-30 | dd/mm/yyyy
| Last Known Good Gas Day*2 |  | dd/mm/yyyy
| Last Gas Day Where Error Present | 2022-12-01 | dd/mm/yyyy
Meter/Metering System |  | Whitwell MTA | CURTOF
Transporter | Upstream | National Grid - NTS
| Downstream | Cadent Gas Limited - DN
Meter Type |  | Orifice
LDZ
Average flow rates for the perceived duration of the Measurement Error |  | Null | MCM/Day
Declared volume of error |  | Null | MCM
Estimated quantity of error |  | Null | GWh
Estimated Significance |  | Low | < 30 GWh
Over or Under Read? |  | Under
Notes
*1 OAD Section D para 5.2.2 applies
*2 OAD Section D para 5.2.3 applies
MCM = million (1x106) cubic meters
Unless stated otherwise all volumes are for the real dry gas at ISO Standard Reference conditions of 15°C and 1.01325 bar.
Unless stated otherwise all energies are calculated using a gross calorific value for the real dry gas at ISO reference conditions of 15°C (combustion) and 15°C and 1.01325 bar (metering).

## Look Up Data
Look Up Table For Offtake Data
Meter/Metering System | Site Type | Short Code | Upstream Transporter/Supplier | Downstream Transporter | Downstream LDZ | Meter Type
(if applicable)
Aberdeen MTA | Offtake | ABEROF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Adnams MRA | Network Entry | <none> | Adnams Bio Energy Limited | Cadent Gas Limited – DN (EA) | EA | Turbine
Adnams MRA/MRB Combined | Network Entry | <none> | Adnams Bio Energy Limited | Cadent Gas Limited – DN (EA) | EA | System
Adnams MRB | Network Entry | <none> | Adnams Bio Energy Limited | Cadent Gas Limited – DN (EA) | EA | Turbine
Alrewas EM MTD | Offtake | ALREOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Orifice
Alrewas WM MTA | Offtake | ALRWOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Alrewas WM MTA/MTB Combined | Offtake | ALRWOF | National Grid - NTS | Cadent Gas Limited - DN | WM | System
Alrewas WM MTB | Offtake | ALRWOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Armadale MTA | Offtake | ARMAOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Aspatria Bio | Network Entry | ASPAOS | BSH | Northern Gas Networks - DN | NO | Rotary Displacement
Aspley MTA | Offtake | ASPYOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Asselby 38B MRC | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Asselby 38B MRD | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRA | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRB | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Atherstone MRA | Inter LDZ Transfer | <none> | Cadent Gas Limited – DN (EM) | Cadent Gas Limited – DN (WM) | WM | Turbine
Atherstone MRA/MRB Combined | Inter LDZ Transfer | <none> | Cadent Gas Limited – DN (EM) | Cadent Gas Limited – DN (WM) | WM | System
Atherstone MRB | Inter LDZ Transfer | <none> | Cadent Gas Limited – DN (EM) | Cadent Gas Limited – DN (WM) | WM | Turbine
Audley NW (Crewe) MTC | Offtake | AUDNOF | National Grid - NTS | Cadent Gas Limited - DN | NW | Orifice
Audley WM (Dunkirk) MTD | Offtake | AUDWOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Audley WM (Dunkirk) MTD/MTE Combined | Offtake | AUDWOF | National Grid - NTS | Cadent Gas Limited - DN | WM | System
Audley WM (Dunkirk) MTE | Offtake | AUDWOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Austrey MTA | Offtake | AUSTOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Aylesbeare MTA | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Aylesbeare MTB | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Bacton MRD | Offtake | BADSOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Turbine
Baldersby MRA | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Baldersby MRB | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Balgray MTA | Offtake | BALGOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Barnes Farm | Network Entry | <none> | Air Liquide UK Limited | Cadent Gas Limited - DN (WM) | WM | USM
Bathgate UMA | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bathgate UMB | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bay Farm | Network Entry | <none> | S&P Biogas Limited | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Biodynamic Nottingham | Network Entry | <none> | Air Liquide Advanced Business & Technologies UK Limited | Cadent Gas Limited - DN (EM) | EM | Ultrasonic
Bishop Aukland MTA | Offtake | BISHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Blaby MTA | Offtake | BLABOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Orifice
Blackrod MTA | Offtake | BLACOF | National Grid - NTS | Cadent Gas Limited - DN | NW | Orifice
Blackrod MTA/MTB Combined | Offtake | BLACOF | National Grid - NTS | Cadent Gas Limited - DN | NW | System
Blackrod MTB | Offtake | BLACOF | National Grid - NTS | Cadent Gas Limited - DN | NW | Orifice
Blyborough MTA | Offtake | BLYBOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Orifice
Bonby | Network Entry | <none> | Air Liquide UK Limited | Cadent Gas Limited – DN (EM) | EM | USM
Bracknell MTA | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | Cadent Gas Limited – DN (NT) | NT | Orifice
Braishfield A MTA | Offtake | BRAAOF | National Grid - NTS | Scotia Gas - DN | SO | USM
Braishfield B MTB | Offtake | BRABOF | National Grid - NTS | Scotia Gas - DN | SO | USM
Brand Sands Bio | Network Entry | BRANOS | TEX | Northern Gas Networks - DN | NO | Rotary Displacement
Bredbury | Network Entry | <none> | Fairfield Bio Energy Limited | Cadent Gas Limited – DN (NW) | NW | Rotary Displacement
Brinklow | Network Entry | <none> | Brinklow Biogas Limited | Cadent Gas Limited – DN (WM) | WM | USM
Brisley MRA | Offtake | BRISOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Turbine
Brisley MRA/MRB Combined | Offtake | BRISOF | National Grid - NTS | Cadent Gas Limited - DN | EA | System
Brisley MRB | Offtake | BRISOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Turbine
Broxburn MTA | Offtake | BROXOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Burley Bank MTA | Offtake | BURLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Burnhervie | Offtake | BURNOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Burton Agnes Bio | Network Entry | BURTOS | AGA | Northern Gas Networks - DN | NE | Rotary Displacement
Caldecott MRB | Offtake | CALDOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Turbine
Caldecott MTA | Offtake | CALDOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Orifice
Caldecott MTA/MRB Combined | Offtake | CALDOF | National Grid - NTS | Cadent Gas Limited - DN | EM | System
Careston MRA | Offtake | CAREOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Chittering | Network Entry | <none> | Pretoria Energy Company Limited | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Choakford MRA | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Choakford MRB | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRA | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRB | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRA | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRB | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coldstream MTA | Offtake | COLDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Coleshill | Network Entry | <none> | Severn Trent Green Power Ltd | Cadent Gas Limited - DN (WM) | WM | Rotary Displacement
Corbridge MRA | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Corbridge MRB | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Cowpen Bewley MTA | Offtake | COWPOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Dagenham | Network Entry | <none> | Refoods UK Limited | Cadent Gas Limited – DN (NL) | NL | Rotary Displacement
Davyhulme | Network Entry | <none> | United Utilities Water Limited | Cadent Gas Limited – DN (NW) | NW | Rotary Displacement
Deanshanger | Inter LDZ Transfer | <none> | Scotia Gas – DN (SO) | Cadent Gas Limited – DN (EM) | EM | Turbine
Derby | Network Entry | <none> | Severn Trent Green Power Limited | Cadent Gas Limited – DN (EM) | EM | Ultrasonic
Dowlais MTA | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Dowlais MTB | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Drointon UMA | Offtake | DRTNOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Ultrasonic
Drointon UMA/UMB Combined | Offtake | DRTNOF | National Grid - NTS | Cadent Gas Limited - DN | EM | System
Drointon UMB | Offtake | DRTNOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Ultrasonic
Drum MTA | Offtake | DRUMOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Dryborough Road | Inter LDZ Transfer | <none> | Cadent Gas Limited – DN (NT) | Scotia Gas – DN (SE) | SE | Insertion DP Device
Dunstall Green MRA | Inter LDZ Transfer | <none> | Scotia Gas – DN | Cadent Gas Limited – DN (NT) | NT | Turbine
Dyffryn Cladach MTA | Offtake | DYFNOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Dyffryn Cladach MTB | Offtake | DYFNOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Easton Grey MTA | Offtake | EGRYOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Easton Grey MTB | Offtake | EGRYOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ecclestone MTA | Offtake | ECCLOF | National Grid – NTS | Cadent Gas Limited – DN | NW | Orifice
Elton MTA | Offtake | ELTNOF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Euston | Network Entry | <none> | Euston Biosgas Limited | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Evesham MTA | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Evesham MTB | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Fairfields Farm | Network Entry | <none> | Fairfield Farm Energy Limited | Cadent Gas Limited – DN (EA) | EA | Ultrasonic
Farningham B | Offtake | FARNBOF | National Grid – NTS | Scotia Gas – DN | SE | Ultrasonic
Farningham MTA | Offtake | FARNOF | National Grid – NTS | Scotia Gas – DN | SE | Orifice
Fiddington MTA | Offtake | FIDDOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Fiddington MTB | Offtake | FIDDOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Finham | Network Entry | <none> | Severn Trent Water Limited | Cadent Gas Limited – DN (WM) | WM | Ultrasonic
Forty Foot Road Bio | Network Entry | FOOTOS | TET | Northern Gas Networks - DN | NO | Rotary Displacement
Ganstead MTA | Offtake | GANSOF | National Grid – NTS | Northern Gas Networks – DN | NE | Orifice
Gilwern MTA | Offtake | GILWOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Gilwern MTB | Offtake | GILWOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Glenmavis MTA | Offtake | GLENOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Glenmavis MTC | Offtake | GLENOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Gosberton MTA | Offtake | GOSBOF | National Grid – NTS | Cadent Gas Limited – DN | EM | Orifice
Gravel Pit Bio | Network Entry | GRAVOS | AGA | Northern Gas Networks - DN | NE | Rotary Displacement
Great Wilbraham MTA | Offtake | GWILOF | National Grid – NTS | Cadent Gas Limited – DN | EA | Orifice
Grindley House | Network Entry | <none> | Grindley Biogas Limited | Cadent Gas Limited – DN (WM) | WM | Rotary Displacement
Guyzance MRA | Offtake | GUYZOF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Guyzance MRB | Offtake | GUYZOF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Hampton Bishop | Network Entry | <none> | STL Energy Limited | Cadent Gas Limited – DN (WM) | WM | Ultrasonic
Hardwick | Offtake | HARDOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Hemswell Cliff | Network Entry | <none> | Air Liquide UK Limited | Cadent Gas Limited – DN (EM) | EM | Ultrasonic
Hibaldstow | Network Entry | <none> | Merlin Renewables Limited | Cadent Gas Limited – DN (EM) | EM | Rotary Displacement
High Headley Bio | Network Entry | HEDLOS | VOL | Northern Gas Networks - DN | NO | Rotary Displacement
Hinckley Town | Inter LDZ Transfer | <none> | Cadent Gas Limited – DN (EM) | Cadent Gas Limited – DN (WM) | WM | Insertion Turbine Device
Holkham | Network Entry | <none> | Egmere Energy Ljmited | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Holmes Chapel MTA | Offtake | HOLMOF | National Grid – NTS | Cadent Gas Limited – DN | NW | Orifice
Horndon B MTA | Offtake | HORNOF | National Grid – NTS | Cadent Gas Limited – DN | NT | Orifice
Howdon Bio | Network Entry | HOWDOS | TEX | Northern Gas Networks - DN | NO | Rotary Displacement
Humbleton MRA | Offtake | HUMBOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Humbleton MRB | Offtake | HUMBOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Hume MRA | Offtake | HUMEOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Hume MRB | Offtake | HUMEOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Hydes Pastures MTB | Inter LDZ Transfer | <none> | Cadent Gas Limited – DN (EM) | Cadent Gas Limited – DN (WM) | WM | Orifice
Ilchester MTA | Offtake | ILCHOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ilchester MTB | Offtake | ILCHOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ipsden MTA | Offtake | IPDNOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Keld MRA | Offtake | KELDOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Kenn MTA | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kenn MTB | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kinknockie MRA | Offtake | KINKOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Kinknockie MRB | Offtake | KINKOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Kirkstead MRA | Offtake | KIRKOF | National Grid – NTS | Cadent Gas Limited – DN | EM | Turbine
Kirkstead MRA/MRB Combined | Offtake | KIRKOF | National Grid – NTS | Cadent Gas Limited – DN | EM | System
Kirkstead MRB | Offtake | KIRKOF | National Grid – NTS | Cadent Gas Limited – DN | EM | Turbine
Lanes Farm Bio | Network Entry | LANEOS | VOL | Northern Gas Networks - DN | NE | Rotary Displacement
Langholm MRA | Offtake | LANGOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Leamington MRA | Offtake | LEAMOF | National Grid – NTS | Cadent Gas Limited – DN | WM | Turbine
Leamington MRA/MRB Combined | Offtake | LEAMOF | National Grid – NTS | Cadent Gas Limited – DN | WM | System
Leamington MRB | Offtake | LEAMOF | National Grid – NTS | Cadent Gas Limited – DN | WM | Turbine
Leeming Bio | Network Entry | LEEMOS | AGA | Northern Gas Networks - DN | NO | Rotary Displacement
Lindholme | Network Entry | <none> | Vulcan Renewables Limited | Cadent Gas Limited – DN (EM) | EM | Rotary Displacement
Little Burdon MTA | Offtake | LBUROF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Littleton Drew MRA | Offtake | LTDWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Lockerbie MTA | Offtake | LOCKOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Lower Drayton Farm | Network Entry | <none> | Thornfield 017 Limited | Cadent Gas Limited – DN (WM) | WM | USM
Lower Quinton UMA | Offtake | LOWQOF | National Grid – NTS | Cadent Gas Limited – DN | WM | Ultrasonic
Lower Quinton UMA/UMB Combined | Offtake | LOWQOF | National Grid – NTS | Cadent Gas Limited – DN | WM | System
Lower Quinton UMB | Offtake | LOWQOF | National Grid – NTS | Cadent Gas Limited – DN | WM | Ultrasonic
Lupton MTA | Offtake | LUPTOF | National Grid – NTS | Cadent Gas Limited – DN | NW | Orifice
Luxborough Lane MTA | Offtake | LUXBOF | National Grid – NTS | Cadent Gas Limited – DN | NT | Orifice
Luxborough Lane MTA/MTB Combined | Offtake | LUXBOF | National Grid – NTS | Cadent Gas Limited – DN | NT | System
Luxborough Lane MTB | Offtake | LUXBOF | National Grid – NTS | Cadent Gas Limited – DN | NT | Orifice
Maelor MUA | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Ultrasonic
Maelor MUB | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Ultrasonic
Malpas MRA | Offtake | MALPOF | National Grid – NTS | Cadent Gas Limited – DN | NW | Turbine
Manor Farm | Network Entry | <none> | Manor Farm Green Energy Limited | Cadent Gas Limited – DN (EM) | EM | Rotary Displacement
Mappowder MTA | Offtake | MAPPOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Market Harborough MTA | Offtake | MKHBOF | National Grid – NTS | Cadent Gas Limited – DN | EM | Orifice
Martyr's Lane (Blackmore Crescent) | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | Cadent Gas Limited – DN (NT) | NT | Insertion DP Device
Matching Green MTA | Offtake | MTCHOF | National Grid – NTS | Cadent Gas Limited – DN | EA | Orifice
Melkinthorpe MRA | Offtake | MELKOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Mepal | Network Entry | <none> | Pretoria Energy Company Limited | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Metheringham | Network Entry | <none> | Heath Farm Energy Limited | Cadent Gas Limited – DN (EM) | EM | Rotary Displacement
Methwold | Network Entry | <none> | Warren Energy Limited | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Mickle Trafford MTA | Offtake | MICKOF | National Grid – NTS | Cadent Gas Limited – DN | NW | Orifice
Mill Nurseries Bio | Network Entry | MILLOS | TET | Northern Gas Networks - DN | NE | Rotary Displacement
Milwich MTA | Offtake | MILWOF | National Grid – NTS | Cadent Gas Limited – DN | WM | Orifice
Minworth | Network Entry | <none> | Severn Trent Water Limited | Cadent Gas Limited – DN (WM) | WM | Rotary Displacement
Minworth 2 | Network Entry | <none> | Severn Trent Water Limited | Cadent Gas Limited – DN (WM) | WM | Rotary Displacement
Nether Howcleugh MRA | Offtake | NETHOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Nether Howcleugh MRB | Offtake | NETHOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Newton Ayecliffe Bio | Network Entry | NEWTOS | BSH | Northern Gas Networks - DN | NO | Rotary Displacement
North Moor Farm | Network Entry | <none> | Rockscape Energy Limited | Cadent Gas Limited – DN (EM) | EM | Rotary Displacement
Oak Avenue | Inter LDZ Transfer | <none> | Cadent Gas Limited – DN (NT) | Scotia Gas – DN (SE) | SE | Insertion DP Device
Pannal MTA | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Pannal MTB | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Park Farm Bio | Network Entry | PARKOS | TET | Northern Gas Networks - DN | NE | Rotary Displacement
Partington MTA | Offtake | PART OF | National Grid - NTS | Cadent Gas Limited - DN | NW | Orifice
Paull MTA | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Paull MTB | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Peterborough Eye MTA | Offtake | PEYEOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Orifice
Peterborough Eye MTA/MTB Combined | Offtake | PEYEOF | National Grid - NTS | Cadent Gas Limited - DN | EA | System
Peterborough Eye MTB | Offtake | PEYEOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Orifice
Peters Green 1 (North Thames) MTA | Offtake | PGRNOF | National Grid - NTS | Cadent Gas Limited - DN | NT | Orifice
Peters Green 1 (North Thames) MTA/MTB Combined | Offtake | PGRNOF | National Grid - NTS | Cadent Gas Limited - DN | NT | System
Peters Green 1 (North Thames) MTB | Offtake | PGRNOF | National Grid - NTS | Cadent Gas Limited - DN | NT | Orifice
Peters Green 2 (South Mimms) MTC | Offtake | PGSMOF | National Grid - NTS | Cadent Gas Limited - DN | NT | Orifice
Peters Green 2 (South Mimms) MTC/MTD Combined | Offtake | PGSMOF | National Grid - NTS | Cadent Gas Limited - DN | NT | System
Peters Green 2 (South Mimms) MTD | Offtake | PGSMOF | National Grid - NTS | Cadent Gas Limited - DN | NT | Orifice
Pickering MTA | Offtake | PICKOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Pitcairngreen MRA | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pitcairngreen MRB | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Plaxton Bridge | Network Entry | PLAXOS | TEX | Northern Gas Networks - DN | NE | Rotary Displacement
Portsdown Hill | Entry Point | None |  | Scotia Gas - DN | SO | Turbine
Poundbury | Entry Point | None |  | Scotia Gas - DN | SO | Turbine
Pucklechurch MTA | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Pucklechurch MTB | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Rawcliffe MRA | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Rawcliffe MRB | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Raynham | Network Entry | <none> | Corbiere Renewables | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Ridge Road Bio | Network Entry | RIDGOS | BSH | Northern Gas Networks - DN | NE | Rotary Displacement
Roehampton Lane | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | Cadent Gas Limited – DN (NT) | NT | Insertion DP Device
Ross WM MTA | Offtake | ROSSOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Ross-On-Wye MRA | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Ross-On-Wye MRB | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Roudham Heath MTA | Offtake | ROUDOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Orifice
Roundhill | Network Entry | <none> | Severn Trent Green Power Limited | Cadent Gas Limited – DN (WM) | WM | Rotary Displacement
Royston MRA | Offtake | ROYSOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Turbine
Royston MRA/MRB Combined | Offtake | ROYSOF | National Grid - NTS | Cadent Gas Limited - DN | EA | System
Royston MRB | Offtake | ROYSOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Turbine
Rugby MTB | Offtake | RUGBOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Saltwick 1 | Offtake | SALTOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Samlesbury MTA | Offtake | SAMLOF | National Grid - NTS | Cadent Gas Limited - DN | NW | Orifice
Scampton | Network Entry | <none> | Grange Farm Energy Limited | Cadent Gas Limited – DN (EM) | EM | Rotary Displacement
Seabank MTA | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Seabank MTB | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Sherburn In Elmet Bio | Network Entry | SHEROS | VOL | Northern Gas Networks - DN | NE | Rotary Displacement
Shorne MTA | Offtake | SHOROF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Shustoke MTA | Offtake | SHUSOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Orifice
Silk Willoughby MRA | Offtake | SILKOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Turbine
Silk Willoughby MRA/MRB Combined | Offtake | SILKOF | National Grid - NTS | Cadent Gas Limited - DN | EM | System
Silk Willoughby MRB | Offtake | SILKOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Turbine
Sotterley | Network Entry | <none> | Biocore AD2 Limited | Cadent Gas Limited – DN (EA) | EA | Rotary Displacement
Soutra MTA | Offtake | SOUTOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Spaldington Bio | Network Entry | SPALOS | TET | Northern Gas Networks - DN | NE | Rotary Displacement
St Fergus MTA | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
St Fergus MTB | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stoke Bardolph | Network Entry | <none> | Severn Trent Green Power Limited | Cadent Gas Limited – DN (EM) | EM | Ultrasonic
Stoke Bardolph 2 | Network Entry | <none> | Severn Trent Water Limited | Cadent Gas Limited – DN (EM) | EM | Ultrasonic
Stranraer MRA | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRB | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stratford MRA | Offtake | STRAOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Turbine
Stratford MRB | Offtake | STRAOF | National Grid - NTS | Cadent Gas Limited - DN | WM | Turbine
Strongford | Network Entry | <none> | Severn Trent Green Power Limited | Cadent Gas Limited – DN (WM) | WM | Ultrasonic
Sutton Bridge MRA | Offtake | SUTNOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Turbine
Sutton Bridge MRA/MRB Combined | Offtake | SUTNOF | National Grid - NTS | Cadent Gas Limited - DN | EM | System
Sutton Bridge MRB | Offtake | SUTNOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Turbine
Tatsfield MTA | Offtake | TATSOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Thornton Curtis MTA | Offtake | CURTOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Orifice
Thrintoft MTA | Offtake | THRNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Tow Law MRA | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Tow Law MRB | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Towton MTA | Offtake | TOWTOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Tur Langton MTA | Offtake | TURLOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Orifice
Walesby MRA | Offtake | WSBYOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Turbine
Walesby MRA/MRB Combined | Offtake | WSBYOF | National Grid - NTS | Cadent Gas Limited - DN | EM | System
Walesby MRB | Offtake | WSBYOF | National Grid - NTS | Cadent Gas Limited - DN | EM | Turbine
Warburton MTA | Offtake | WARBOF | National Grid - NTS | Cadent Gas Limited - DN | NW | Orifice
Wardely Bio | Network Entry | WARDOS | AGA | Northern Gas Networks - DN | NO | Rotary Displacement
Welbeck Colliery | Network Entry | <none> | Biogas Meden LTD | Cadent Gas Limited – DN (EM) | EM | Rotary Displacement
West Winch MTA | Offtake | WINCOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Orifice
Weston Point MTB | Offtake | WESTOF | National Grid - NTS | Cadent Gas Limited - DN | NW | Orifice
Westry | Network Entry | <none> | Air Liquide UK Ltd | Cadent Gas Limited – DN (EA) | EA | Ultrasonic
Wetheral MTA | Offtake | WETHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Whitwell MTA | Offtake | WHITOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Orifice
Whitwell MTA/MTB Combined | Offtake | WHITOF | National Grid - NTS | Cadent Gas Limited - DN | EA | System
Whitwell MTB | Offtake | WHITOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Orifice
Widnes | Network Entry | <none> | Refood UK Limited | Cadent Gas Limited – DN (NW) | NW | Rotary Displacement
Winkfield 2 MTB | Offtake | WNKSOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Winkfield MTA | Offtake | WINKOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Winkfield NT MTC | Offtake | WINTOF | National Grid - NTS | Cadent Gas Limited - DN | NT | Orifice
Wytch Farm | Network Entry | <none> | Perenco | Scotia Gas - DN | SO | Orifice
Yelverton MTA | Offtake | YELVOF | National Grid - NTS | Cadent Gas Limited - DN | EA | Orifice
| Over/Under Indicator | Error Magnitude |  | Error Status
| Over | High | >= 50 GWh | Error Notified
| Under | Low | < 30 GWh | MER in Compilation
|  | Medium | >= 30, < 50 GWh | SMER in Compilation
Passed to NTS
MER Published
SMER Published
Awaiting First Available Invoice
Invoiced
Closed / No Rec Required

## Extract for Register
Unique Reference Number | DN Reference | Description | Offtake | LDZ | Downstream Transporter | Significance Low <30GWH Medium >=30<50GWh High >=50GWh | Declared volume of error (MCM) | Estimated quantity of error (GWh) | Discovered | Error First Notified | First Gas Day Where Error Present or; | Last Known Good Gas Day | Last Gas Day Where Error Present | Latest Notification Update | Latest Error Status | Live/ Closed
EA019 | MER/CAD/226/22 | The incorrect orifice plate calibration reference temperature was entered into the Omni flow computer due to ambiguity between the environment temperature and the orifice plate surface temperature on the calibration certificate. The error is approximately -0.001217% which is approximately 100 times smaller than the 0.1% of daily flow required for a reconcilable MER. | Whitwell MTA | 0 | Cadent Gas Limited - DN | Low | Null | Null | 2022-11-18 | 2022-12-29 | 2022-07-30 | 0 | 2022-12-01 | 2022-12-29 | Closed / No Rec Required | Closed